## Slide 1
Modeling and Analysis of SVPWM
Based Dynamic Voltage Restorer

## Slide 2
Introduction
Structure of DVR
Simulation of SVPWM based DVR
Conclusions
Simulation of SVPWM
Outlines

## Slide 3
Introduction
Power quality problems
Voltage magnitude variations
Frequency variation
Three phase unbalance
Voltage fluctuations
harmonics
Voltage notching
noise
Under voltage
Supply interruption
Voltage sag
over voltage
Voltage swell
Fast voltage events
Voltage magnitude steps
Power quality problems
variations
events
Voltage sag
0.5 cycle
3 sec
1 min
Normal operation
momentary
Voltage
sag
temporary
Sustained interruption
Undervoltage
Overvoltage
Voltage
swell
Notch/Transient
10%
90%
110%
Transient
Event duration
IEEE standard 1159-1995

## Slide 4
<number>
<number>
Introduction
Voltage sag mitigation
Motor-generator set
Electronic tap changers
Uninterruptable Power Supply (UPS)
Dynamic Voltage Restorer (DVR)
Types of
mitigation equipment
Static VAR compensators

## Slide 5
<number>
<number>
<number>
<number>
<number>
<number>
<number>
Dynamic Voltage Restorer (DVR)
Source
Normal Load
Sensitive
Loads
measuring
interface
controller
inverter
DC source
filter
Injection
transformer
DVR
Structure of Dynamic Voltage Restorer

## Slide 6
<number>
<number>
<number>
<number>
<number>
<number>
<number>
<number>
DVR Design Procedure
The design procedure can be divided into
    The power circuit design
    The control Algorithm

## Slide 7
<number>
<number>
<number>
<number>
<number>
<number>
<number>
<number>
<number>
The power circuit is composed of;
Injection transformers
Filter
inverter
DC source
DVR Design

## Slide 8
2- adjusting the proper firing pulses
for the inverter
The controller has two main jobs;
1- Sensing the sag occurrence
Vβ_err
<number>
<number>
<number>
<number>
<number>
<number>
<number>
<number>
The control algorithm
abc/αβ
αβ/dq
SPLL
Θ-30
dq/αβ
1/√3
SVPWM
Va
Vb
Vc
Vα
Vβ
Vd
Vq
θ
Vd_ref
Vq_ref
Vd_err
Vq_err
Vα_err
Switching pulses
Sag occurrence
adjusting firing pulses
DVR Design
Voltage mag. control
Voltage phase control

## Slide 9
The following data are the same for the simulation and the practical system;
Source: Vs = 110 V (line to line)
Zs = 1.3 Ω
Load: three phase balanced load 120 Ω per phase
Filter: L = 370 µH
C = 90 µF
Injection transformers:
Turns ratio = 1:1 ratings = 45V, 2A
DC source for the inverter: Vdc = 70V
<number>
<number>
<number>
<number>
<number>
<number>
<number>
<number>
Test system description
Case Study

## Slide 10
.
.
.
.
.
.
The simulation of the power circuit:
<number>
<number>
<number>
<number>
<number>
<number>
<number>
<number>
Simulation
Case Study
.
source
Sag generator
.
Sag control
Bypass switches
Bypass switches control
Load
Injection transformers
Three phase filter
From
inverter

## Slide 11
The simulation of the control circuit:
<number>
<number>
<number>
<number>
<number>
<number>
<number>
<number>
Simulation
Case Study
to
filter
.
inverter
SPLL
Abc to αβ
transformation
αβ to dq
transformation
.
d_ref
SPLL to generate θ
q_ref
dq to αβ
transformation
θ-30 to compensate delta/open
/√3 to compensate delta/open
SVPWM to generate pulses
Ts
DC source
inverter

## Slide 12
<number>
<number>
<number>
<number>
<number>
<number>
<number>
<number>
simulation results
Case Study
The load voltage: is the phase voltage of the load
The DVR voltage : is the injected voltage in series
with the load voltage
<number>
<number>
<number>
<number>
<number>
<number>
<number>
<number>
<number>
DVR voltage
Load voltage

## Slide 13
<number>
<number>
<number>
<number>
<number>
<number>
<number>
<number>
Load Voltage
DVR Voltage
Sag start
For sag 20%
DVR is off
For sag 20%
DVR is on
Load Voltage
DVR Voltage

## Slide 14
<number>
<number>
<number>
<number>
<number>
<number>
<number>
<number>
Load Voltage
DVR Voltage
Sag start
For sag 25%
DVR is off
Load Voltage
DVR Voltage
For sag 25%
DVR is on

## Slide 15
<number>
<number>
<number>
<number>
<number>
<number>
<number>
<number>
Conclusions
The following outcomes may be concluded:
DVR is a function/price compromised solution to mitigate voltage sag especially at medium level loads
The simulation of three phase DVR using SVPWM technique to control its inverter was presented
Practically, the DVR can respond very fast to mitigate voltage sag (<0.5 cycle) which is perfect for almost all sag sensitive loads
The DC source capacity imposes a limitation on the restoration capability of the DVR