Project Report ON Gas Plant

N. T. P. C.

(NATIONAL THERMAL POWER CORPORATION)

Albert Einstein said “We owe a lot to the Indians, who taught us how to count, without which no worth while scientific discovery could have been made. From counting to launching satellites, to making supercomputers India has done it all. Maintaining the same zeal in the power sector are various power companies, the most prominent among which is NTPC. The National Thermal Power Corporation was established in 1975 to play a major in the Indian power sector. Today with an installed capacity of 18,351MW the corporation is looking ahead with an ambitious corporate plan to achieve a capacity of 30,000MW by year 2007 and 40,000MW by year 2012. Operating 13 coal based and 7 gas based stations, NTPC with its share of about 19% of India’s total capacity generates 24.4% of the country’s power.

A consistent high level performer in operations NTPC provides the benchmark for the Indian power sector. Inspired by a glorious past and brilliant present, NTPC is heading towards a brighter tomorrow. Every milestone achieved is a dream come true for its 23,000 dedicated employees working in its plants across the country.

BREAKING NEW GROUNDS

As part of the corporate growth strategy, NTPC is diversifying into hydel and non conventional energy development. As part of this plan NTPC and ABB Alston have launched their 50:50 joint ventures. The company will seek business for renovation and modernization of power plants. Also NTPC is presently in the process of tying up LNG supplies for the expansion of its gas based station.

FINANCIAL MILE STONES

The corporation achieved a net turn over Rs 16479.24 crore. The provisional profit, after tax, rose to Rs 3401.96 crore registering an improvement 20.81% over the previous year profit of Rs. 2815.73 crore. In the Asiaweeks ranking of the top 1000 companies of Asia-Pacific region, NTPC has improved its ranking to 299 from the previous year ranking of 344 in terms of sales volume.

LEADING THE RACE

During 1998-99, the corporation an all time high of 109.5 billion units of electricity at a plant load factor of 76.6% and availability of 89.36%. With the expertise gained over the years in power station management, NTPC has successfully revived three sick coal based power stations namely Badarpur (705MW), Unchahar (420MW) and now 840MW and Talcher thermal (460MW).

GENERATING GREEN POWER

The corporation has been identified as implementing agency for “Green House Gas Emission Prevention Project” by the USDOE and USAID. NTPC has set up a “Centre for Power Efficiency and Environmental Protection” (CENPEEP) which functions as a resource centre for development and dissemination of latest technologies. For the 12th consecutive year, NTPC achieved all the targets set for it under the memorandum of understanding with the Government of India and was rated excellent.

- Engineering and Operation services awarded ISO9001

- Contracts Division accredited with ISO9002

- Vindhyanchal, Korba, Rihand, Kawas, Gandhar stations awarded ISO9002

- Dadri station accredited with ISO14001

NTPC-DADRI

(An ISO 14001 & 9002 Certified Station)

NTPC Dadri was set up in the central sector in the year 1975  in response to widening demand and supply gap with the main objective of planning, promoting & organizing  an integrated  development of thermal power in India .Ever since its inception, NTPC  has never looked back  and the corporation is treading  steps of success one after the other. The only PSU to have achieved excellent rating in respect of MoU targets signed with the Government of India each year.

NTPC is poised to become a 40000 MW giant corporation by the end of 11th plan i.e. 2012 AD. Lighting up one fourth  of the nation, NTPC has installed capacity of 19291 MW from it’s 13 coal based stations and 7 gas based stations as on 31:03:2000  with it’s commitment to provide quality power, all the operating stations of NTPC located in the national capital region & western region have acquired ISO 9002 certification . The service groups like Engineering, contracts, Materials and operation services have also bagged the ISO 9001 certification. NTPC Dadri, Ramagundam, Vindhyachal and Korba stations have also bagged ISO 14001 certification.

STATION AT A GLANCE

NTPC Dadri is the modal project of NTPC. It is situated 60 km away from Delhi in the Gautam Budh Nagar district, Uttar Pradesh. The station has an installed capacity of 1669MW of power-840 MW from coal based units and 829 MW from gas based units. The station is excelling in performance ever since it’s commercial operation. Consistently in receipt of meritorious productivity awards, the coal based units of  the station stood first in the country in terms of PLF  for the financial year 1999-2000 by generating an all time national high PLF of 96.12%. With the most modern O& M practices, NTPC Dadri is committed to generate clean and green power.

The power station also houses the first HVDC station to the country (now under the control of PGCIL) with a power handling capacity of 1500 MW. Towards sustainable development and Eco friendly power generation, the station has taken up task under the green house gas pollution prevention project (GEP project) in association with the centre for power efficiency and environmental protection CENPEEP-NTPC & USAID. The station has bagged ISO 14001 &ISO9002 certification during the same financial year 1999-2000, certified by agency of international repute M/s DNV Germany respectively.

COAL TRANSPORTATION AND HANDLING SYSTEM

NTPC Dadri is a rail fed power station and the coal supply is linked with Piparwar block of north Karanpura coal fields Ltd in Bihar state, located 1200 Km away from the power station from Dadri railway station. The coal rakes are brought to NTPS siding and unloading points through railway track which is totally electrified and constructed by NTPC Dadri. The station has facility for receiving coal through BOBR rakes at wagon tippler. There are two streams in CHP, each having a capacity of 1400 MT/hour. As the station is a rail fed station it is expected to maintain a coal stock of approximately One month. The stock yard has a capacity of 5 lacs MT and coal can be stored /retrieved through a Stacker Reclaimer. From track hopper or stock yard, coal is fed into coal bunkers through conveyors after being crushed to a size of less than 20 mm. Since April 1997, the station has also starting receiving washed coal from washery set up at Piperwar in Bihar. Effective dust suppression and dust extraction systems are installed to minimise the fugitive dust emission during the unloading and handling of coal.

POWER EVACUATION

Dadri switchyard is the largest switchyard in country, in terms of power evacuating capacity. With a power handling capacity of 4500 MW, it is the most critical switchyard in the northern grid. The generating voltages of coal and gas units are stepped up to 220 KV by the respective generator transformers are connected to separate 220 KV switchyard. Further both the stations are connected to the same 400 KV switchyard through separate two banks each of 500 MVA interconnecting transformers of 400/220 KV.

The system has also connected to 500 KV Rihand – Dadri HVDC terminal for evacuation of 1500 MW power. The Inter state 400 KV lines emanating from Dadri switchyard are Malerkotla (Punjab), Muradnagar (UP), Ballabgarh (Haryana),Mandola(DELHI) and Panipat (BBMB system). Through the Mandola double circuit lines, Dadri 400 KV switchyard feeds up to 1500 MW to the Delhi system .On the preventive maintenance front for the first time in the country, the practice of periodical Hotline water washing is adopted, both for 220 KV 400 KV bays.

ENERGY CONSERVATION

In NTPC a full fledged Energy Conservation group is dedicated to the mission of conserving energy. he focus is on Optimising auxiliary power consumption, reducing consumption of fuel oil and lub oil, reducing specific coal consumption by improving heat rate, reducing DM water consumption and stopping wastage of which can be put to use. NCPS is vigorously pursuing the promotion of non conventional sources of energy. Three numbers 500 LPD solar water heaters are installed at guest house and plant canteen. Solar photo voltaic street light system and six solar photo voltaic traffic warning lights have been installed and are functional at NCPS. Further on anvil is the installation of the street light system in other areas along with installation of solar photo voltaic water pumping system in the plant area for horticulture purposes.

ASH HANDLING SYSTEM

Station is first in the country to adopt Dry ash handling system, handling about 1.5 million tons of ash per annum. The system is highly eco friendly and redresses all the negative environmental effects Fly ash and Bottom ash is handled separately   and taken to ash mount on conveyors from respective storage bins. The construction of ash mount is unique. The mount shell caters to the storage of ash for the entire plant life and would be constructed to a final height of 55 meters with 140 acres as the top surface area. Ash mount construction requires only 1/3rd   land requirement and extremely low water requirement of 2% in comparison to the conventional wet ash disposal system. Nature is recreated on the finished mount slopes by extensive turfing, tree plantation etc. Finished mount slopes can be commercially exploited to generate revenue

COAL UNIT                                      GAS UNIT

| Topics | Specifications | Topics | Specifications |
| --- | --- | --- | --- |
| STATION CAPACITY :- FUEL:- COAL SOURCE:- COAL TRANSPORTA-TION:- WATER SOURCE:- CONSUMPTIVE REQUIRMENT:- ASH DISPOSAL:- CHIMNEY:- COOLING TOWERS:- BOILER:- TURBINE:- GENERATOR:- | 840 MW (4 x 210 mw units) 100% COAL PIPARWAR BLOCK OF NORTH KARANPURA COAL FIELDS IN BIHAR SITUATED ABOUT 1200 KMS FROM STATION BY INDIAN RAILWAYS MAINLY THROUGH BOTTOM DISCHARGE WAGONS UPPER GANGA CANAL, DURING CLOSURE OF CANALS THROUGH A NETWORK OF TUBEWELLS 50 CUSECS PER DAY DRY ASH DISPOSAL RCC MULTY FLUE CHEMNEY WITH STEEL FLUE-225M HIGH NATURAL DRAFT TOWERS SEPARATE FOR EACH UNIT OF 120 MTR HEIGHT MAKE:BHEL DESIGN:COMBUSTION ENGG USA TYPE:NATURAL CIRCULATION, BALANCED DRAFT DOUBLE PASS SINGLE DRUM,DIRECT PULVERIZED/ OIL FIRED,DRY BOTTOM TYPE MAKE:BHEL DESIGN:KRAFTWERK UNION GERMANY TYPE: TANDOM COMPOUND, REGENERATIVE, REHEAT, CONDENSING, THREE CYLINDER HAVING SINGLE FLOW HP TURBINE,DOUBLE FLOW IP & LP TURBINE. MAKE:BHEL TYPE:THW-210-2 TWO POLE CYLINDRICAL, STEAM TURBINE DRIVEN | STATION CAPACITY FUEL GAS SOURCE TYPE OF STATION COOLING WATER SOURCE NUMBER OF MODULES GAS TURBINES WASTE HEAT RECOVE-RY BOILER GENERATOR (GAS TURBINE) STEAM TURBINE GENERAT-OR(STEAM TURBINES) | 829 MW NATURAL GAS FROM HAZIRA THROUGH HBJ PIPELINE COMBINED CYCLE STATION UPPER GANGA CANAL,DURING CLOSURE OF CANALS THROUGH A NETWORK OF TUBEWELLS TWO. EACH MODULE COMPRISING OF 2-GAS TURBINES AND 1 STEAM TURBINE MAKE: SIEMENS AG GERMANY TYPE:V 94.2 MAKE: BHEL TYPE:VERTIC-AL, FORCED CIRCULATION DUAL PRESSURE MAKE: SEIMENS AG GERMANY TYPE: TLRI-108/41 MAKE:BHEL TYPE:TWO CYLINDER REACTION CONDENSING MAKE:BHEL TYPE:THRI-100-36P |

UNIQUE FEATURES

- Only power station in the country housing both coal based and gas basedunits-840 MW coal units and 829 MW gas units

- Largest gas station in the country

- Largest switchyard in country with power handling capacity of 4500 MW being one of the major contributors of power to the capital and neighbouring states.

- Station also houses 1500 MW HVDC converter station, the first of its kind in India, managed presently by power grid corporation of India LTD

- Largest dry ash handling plant in Asia and unique construction of ash mount

- Intensified thrust on rehabilitation activities to take care of project affected families

- State of art Digital Data Control MIS installed at coal units

- Natural Draft Cooling Towers of 120 meter height installed for coal units.

- State of art computer networking for vital systems.

RECOGNITIONS

- First coal and gas based power station  in the country, to be certified  for ISO 14001.Certificate received from agency of international repute M/s DNV Netherlands

- Coal and gas based station also certified for ISO 9002 in the same financial year 1999-2000, by M/s DNV Germany an agency of international reputation.

- Best performing station amongst NTPC stations for third consecutive year 1999-2000.

- IOC rolling trophy for “Minimum Oil Consumption”  for three years in succession i.e.1996-97,1997-98,and 1998-99

- NTPC trophy for energy conservation for two years i.e.1996-97, 1997-98.

- NTPC trophy for productivity and rajbhasha for year 1999-2000.

- Runners up prize for” Ash Utilisation &its safe disposal” from council of power utilities year 1999.

- “British safety council award” for the year 1998-1999.

- First recipient for “Shreshta Suraksha Puraskar” from national safety council of India for the period 1995-98.

- Meritorious productivity awards by ministry of power every year since 1995-96.

- Gold medal for coal and gas station under meritorious productivity awards for year 1997-98.

- NTPC trophy for environment protection and improvement for the year 1997-98

GAS PLANT (DADRI)

Location                                   			 : The project site is located 				   between mat branch canal and 			   upper Ganga canal in  					   Ghaziabad district of U.P. at a 			   distance of about 6.75 km from 			   Dadri town.

Plant Capacity                          		: 817.48 MW

Mode of Operation                                       : Base load

Fuel							: Natural has (Main fuel), HSD 								  (contingency)

Gas requirements					: 3.00 MCMD

Gas transportation				: Babrala-Delhi section of H-B-J 							  pipeline extension

CW system						: Closed cycle cooling water 								  system with Induced draft 								  cooling towers and make water 							  supply from Dehra feeder canal, 							  main branch of upper Ganga 								  canal.

Power Evacuation				: SEB's 220KV Grid & NTPC's 							  400KV Grid in Northern region

Environmental Aspects				:

1. Water Pollution				: Effluent from Demineralising 								  and softening plants is 									  neutralized before being sent 								  out.

2. Air Pollution					: Practically nil.

Unit Commissioned				:

GT  	: 	I	JAN.  92

II	MAR. 92

III	JUN.   92

ST	 	:	I	MAY. 93

II	AUG. 93

# PLANT LAYOUT

## GENERAL PLANT LAYOUT

The plant layout has been prepared in keeping with the plot configuration, area contours, requirement of the plant water system and power evacuation route.

The power station has been located nearest to the canal on high ground so that it is safe from flooding in the events of breach of canal embankment. CW pump house has been located near the powerhouse block and the cooling towers.

The water pretreatment plant and DM plant are located adjacent to both the powerhouse and CW pump. The 200/400KV switchyard has been located in front of the power station. The 200KV switchyard control room is accommodated in the main building itself & the station transformers have also been accommodated in the main transformer yard complex.

Space for railway marshaling yard has been kept so that a spur can be taken in future if required. Future oil unloading header from railway siding has been conceived. Space has been kept for liquid oil installation and oil unloading pump house.

The GAIL terminal for receiving gas is within boundary of plant site. Administrative building has been placed adjacent to the plant entry gate and has been provided with independent access.

Permanent store has been located near the power station proper. The canteen is located in the clean area near the works center of largest number of employees.

The colony is located on the approach road to the plant site. The distance between the plant and colony is less then one km.

Construction offices, stores and other facilities required during construction these have been located in an area free from permanent installation.

### MAIN PLANT LAYOUT

The GTGs & STGs are housed in turbine hall, with two numbers STGs placed longitudinally in the center of the hall, whereas two numbers each of GTGs are placed on either side of north of turbine hall. Steam cycle equipment except WHRB is located in steam turbine portion turbine hall. There are five numbers of EOT cranes one for each pair of STGs, GTs and GTGs. The plant central control room, including 220KV switchyard control is located at 11.5m level. Each GTG is having one local control panel located near the GT pedestal itself. The transformer yard is located on the southern side of the turbine hall. Switchyard is located further south of the transformer yard.

OPERATION

In this plant unlike coal as in the thermal plant gas is used as the fuel. Some times gas and HSD mixture is also used as the fuel for igniting the gas as the fuel pressured with high temperature is used the ambient air is first filtered and is then brought to the compressors where the temp and pressure of the air rises.

Temperature of the air is usually 340-360 degree celsius while pressure is usually of 7-10 bars. The compressed air is send to the combustion chambers, which are located on either direction of the turbine. The fuel gas is supplied to the burners in the combustion chamber. Since the air in the combustion chamber is at high temperature it burns the fuel gas. The fuel gasses, which are at much higher temperature i.e., nearly 1040-degree celsius are sent to the turbine. The hot gasses rotate the turbine blades that are mounted on a rotor. The rotor of the turbine is coupled with the generator rotor. The rotor rotates at the approx. 3000rpm. The gasses leaving the turbine are still at high temperature that is nearly equal to 500-550 degree Celsius. This air is then sent to the WHRB where water supply is maintained with the help of HP & LP water pumps. The water is heated in the boiler thus steam is generated. The steam from the HP & LP water pipes is sent to the steam turbine.

Apart from their comparatively low capital cost per installed KW and short installation time, an outstanding advantage of the gas turbine/combined cycle plants is their ability to startup quickly and their fast response to load changes. A combined cycle plant can be started and brought to about 65% of its full load in about 15 minutes, and can be taken to its full load in about one hour when starting from a warm condition and about 3 hours when starting from a cold condition.

Further there is no requirement of keeping the auxiliaries in operation when the generating units are idling during off peak hours. The present gas price also dictates that combined cycle plant be backed down during off peaks hours, as their incremental fuel cost per KWh would be 2 to 3 times that of coal fired thermal stations. The combined cycle plants have a short time peaking capability of about 5%, and this could be utilised during high load demanded and system crisis situations.

BASE LOAD OPERATION

However, for combined cycle plant along the H-B-J pipe line, it may not be desirable to have wide variation in the withdrawal rate of natural gas from the pipeline due to limitations of the gas supply system, and it may become necessary to operate these plants at more or less constant load. The combined cycle power plants are suitable for this mode of operation as well, due to their higher efficiency.

PART LOAD OPERATION

The main consideration during the operation of combined cycle plants at different loads is obtaining the best possible efficiency. Combined cycle mode is therefore to be retained in operation at partial loads also, by switching off one of the gas turbines alongwith its WHRB, whenever the module load is to be brought down to about 50% for a significant duration. The steam turbine is switched off only when the module load is to be reduced bellow about 25% of its full load rating a few hours.

BLACK START FACILITY

For starting up of the main gas turbine, and to meet all the associated emergency auxiliary power requirement in case of grid failure or a total black out (when auxiliary power is not available from the external sources),  a gas turbine generator is provided as black start facility. It is capable of cranking up one gas turbine at a time. The combined cycle plant is accordingly self starting, and is source of startup power for the conventional steam power stations in the grid, in case of system emergencies.

ORIGINAL SETUP

The plant is headed by a plant manager, a person in the rank of not less than DGM, who has overall administrative as well as technical control of the station and reports to the general manager of gas plant (GP). For effective operation, maintenance and administration of the plant adequate number of suitable, technical and administrative personnel are posted under him.

SALIENT FEATURES

Type of station				: Combined cycle power plant

Station capacity				: 829.28 MW

Fuel						: Main – natural gas

Alternate fuel HSD

Source gas					: Hazira

Transportation				: Through HBJ pipeline

Consumption				: 4.0 MCMD

Cooling Water source			: Upper gang canal Dehra Head work.

During closure of UGC, through 							  network of tube wells

Start up Power				: Black start DG set 2.6MVA capacity

Efficiency:-

Open cycle					: 2692 KW / KWH

Combined cycle				: 1748 KW / KWH

FUELS

Gas turbines are capable of burning a range of fuels including naphtha, distillates, crude oil & natural gas.

Natural gas is an ideal fuel because it provides high thermal efficiency & reliability with low operation & maintenance cost.

Duel fuel system are commonly used, enabling the gas turbine to burn back up fuels when the primary fuel source is not available. This system can also be designed to fire both fuels simultaneously.

### COMBINED CYCLE

Combined cycle power plant integrates two-conversion cycles namely-

- Brayton cycle (gas turbine)

- Rankine cycle (conventional steam power plant)

## BRAYTON CYCLE

Gas turbine plants operate on Brayton cycle in which air is compressed and heated in the combustor by burning fuel. Combustion produced is allowed to expand in the turbine and turbine is coupled with a generator.

In actual process losses occurs from the fact that compression and expansion are not performed entropically but polytropically conditioned by heat expansion & heat supply (compression) caused by various flow and fraction losses. The Brayton cycle is chosen due to high temperature exhaust (500°C to 550°C) of the gas turbine.

## RANKINE CYCLE

The conversion of heat energy to mechanical energy with the aid of steam is carried out through this cycle. The initial state of the working fluid is water, which at certain temperature is compressed by a pump and fed to the boiler. In the boiler compressed water is heated at constant pressure.

The efficiency of gas turbine cycle is 30% and the efficiency of Rankine cycle is 35%. The overall efficiency of combined cycle comes to 48%.

# TYPES OF COMBINED CYCLE

There are basically two types of combined cycle

- Unfired combined cycle

- Fully fired combined cycle

# UNFIRED COMBINED CYCLE

In this system the exhaust gas is used only for raising steam to be fed to the steam turbine for power generation. Conventional fossil fuel fired boiler is replaced with a feat recovery steam generator (HRSG). Exhaust gas from the gas turbine is led to the HRSG where heat of exhaust gas is utilized to produce steam at desired parameter as required by steam turbine.

# FULLY FIRED COMBINED CYCLE

In this system the feat of exhaust gas from gas turbine is used for two purposes. Heat contained in the exhaust gas is used to heat fed water to desired temperature. This leads to reduction or eliminating of the extraction steam requirement from the steam turbine.

Gas turbine exhaust contains 14% to16% oxygen and can be used as hot secondary air in the conventional fossil fired furnaces. So the heat required to heat the secondary air will be saved and can be used for other purposes.

PRINCIPLE OF OPERATION

Air is drawn into the compressor where it is compressed to a static pressure several times that of the atmosphere and at increase temperature. This compressed air goes into the combustion chamber, where fuel is injected. The fuel burns in the combustion chamber. The product of combustion chamber i.e. burned high temperature gas passes through the turbine blades where the gas expands developing motive power to turn the turbine rotor. A part of the power developed by the hot gas is used to run the compressor and auxiliaries while the rest is used to generate electrical energy by driving the generator.

When the fuel gas from the gas turbine is passed directly in to the atmosphere, it is called open cycle operation. When the hot gas from the gas turbine exhaust is passed through WHRB to generate steam for running the turbine it is known as combined cycle operation.

# ADVENTAGES

- Low installation cost

- Low installation period

- Better reliability

# Low installation cost:

The installation cost of combined cycle power plant is approximately 70% of a conventional coal based plant of same capacity.

Low gestation period:

The power from combined cycle power plant can be obtained in to phases i.e. two third power, obtainable from gas turbines, is available within 16-18 months and the balance in next 6 months. This is much lower then the gestation period for conventional thermal power plants, which is around 40-60 months.

Better reliability:

Combined cycle power plant has a reliability factor of 85%-95% as compared to 60%-65% for conventional coal fired power plants.

Basic Elements of a Combined Cycle Power Plant:-

- Gas turbine (GT)

- Waste hest recovery boiler (WHRB)

- Steam turbine (ST)

GAS TURBINE

Make							: Siemens AG, Germany

Type 							:  V 94.2

Capacity 						: 131.3MW

Gross power 					: 284.2MW

Turbine efficiency 					: 32.7%

Design inlet temperature				: 1060C

Critical speed of turbine 				: 3000rpm

Self sustaining speed 				: 2100rpm

Quantity of air required for 			: 50kg/sec

cooling & sealing

## Types of tertiary blades of rotor disk		: Fire free roots

Type of Governing Starting Device 		: Electro hydraulic

- Type 						: Starting frequency converter

- Rated power				: 2900kw

3.   Time from barring speed to 		: 4min

synchronization

Rates of loading:

Normal (MW/min)			: 11

Fast (MW/min)			: 30

Heat rate of gas turbine (Kcal/KWh) on natural gas firing:

Peak					: 2674

100%					: 2692

80% 					: 2789

60%					: 2997

25%					: 4408

Heat rate of combined cycle (Kcal/KWh) on natural gas firing:

Peak					: 1724

100%					: 1748

80%					: 1796

60%					: 1925

Gas Turbine Inlet Temperature:

Peak					: 1100

100%					: 1060

80%					: 942

60%					: 826

25%					: 625

Main Fuel				: Natural Gas

Alternate fuel			: HSD

Gas Turbine Compressor

Manufacturer					: Siemens KWU

Type							: Multistage axial flow

No. of Stages					: 16

Guide vane compressor				:  1.Variable type at the inlet of 								      the

2. Fixed type at the exit of the

compressor

Compression Ratio					: 10.2

Air flow rate at 27C				: 404 KG/sec

Compressor efficiency				: 88.2%

No. of bleeds					: 2

Type of fixing of rotor disk			: Hirth serration

Type of fixing of blades of rotor		: Dove tail

Type of fixing of rotor				: Central Bolt

Compressor washing method			: Wet cleaning

Washing agents					: Ardsox 6322 or equivalent

Frequency						: Depending upon Compressor

Water tank Capacity				: 0.5m³

Type of pump					: KSB: MOVI

The gas turbines are heavy duty industrial type machines with axial air compressor section and gas turbine section on the same shaft with an intermediate section combustion chamber for fuel gas injection and combustion.

Each gas turbine is connected to its machine generator. The governing system controls the fuel input and the closure of the fuel valve is adequate to arrest any abnormal speed rise. Moreover, as the compressor is on the same shaft, with proper bleed, enough drag exists to break the unit sharply.

The governing system has the following controls-

- Speed/frequency control

- Load control

- GT exhaust temperature control along with peak/base select selection

It is difficult to measure the gas temperature at the inlet to gas turbine, hence the exhaust temperature from the gas turbine is measured at multiple points around the exhaust periphery. A scale of the temperature is a good measure for evaluating the fuel distribution and inlet gas temperature. The compressor being a volumetric compression device, the mass flow through turbine depends on the density of air at inlet and hence ambient temperature relative humidity and altitude.

As the maximum fuel input is restricted by the gas inlet temperature to the gas turbine (after the combustion section and assessed by past proved correlation from gas turbine exhaust temperature), the output of the gas turbine varies with the above parameters and also by later additional friction in air or gas path due to fouling.

The gas turbine during startup remains under speed control on a preprogrammed basis. The unit is cranked to the preset speed, firing is initiated and the unit is further speeded to the synchronizing speed. The cranking device which envisaged a static frequency converter is switched off at preset self sustaining speed. It is evident that the air flow is much less at the startup and hence the fuel feed is accurately controlled to avoid excessive gas temperature rise or prolonged startup.

Once the gas turbine is synchronized, it is loaded at preset rate to a preset value. The controls can then be set so that the unit either holds a preset load or varies with changes in frequency with adjustable drop characteristic.

It is expected that initially the gas turbine would to the bypass stack with damper to the WHRB closed. It can even be started with WHRB in line.

Normal protection against tube failure, overspeed, and high gas exhaust temperature provides trip signal to the GT and the fuel inlet valve would snap shut. The trip would also occur in case faults of class A in the generator, transformer and the bus duct section.

The gas turbine startup is monitored and controlled by discrete sequence. The sequence can be allowed to proceed on auto mode. The gas turbine has to be cranked up to about 20% speed to establish sufficient air flow to initialize ignition and fuel entry. In some continental design unit frequency is done by a static frequency converter module feeding the main generator, use as motor for startup.

A diesel generating set has also been made to furnish adequate emergency power for cranking one GT unit along with basic plant auxiliaries in case of grid failure. This permits the station to start without external power during a major upset and the station is of immense value in providing startup power for other large coal based units in the area.

Once the first GT is started and loaded, other gas turbines can be fed power from the station. This small emergency set has a small integral diesel engine with a DC motor within its skid for cranking.

The main feature of this gas turbine is the simple design, one compressor, one combustion chamber with one burner, a five stage turbine arranged on a common shaft with the seventeen stage compressor, the shaft being mounted on two general bearing, the axial thrust absorbed by one thrust bearing as well as an exhaust gas diffuser which permits an easy connection to a waste heat boiler.

The single combustion chamber was mounted at the side of the GT and via a U-shaped double piping, connected to the gas turbine to reduce the size of the combustion chamber so that it is now arranged directly above the gas turbine. A dual fuel burner makes it possible, simultaneously or alternately to use gaseous or liquid fuels at improved combustion conditions.

In the gas turbine, the power for driving the compressor and the generator is produced. This is supplied to the turbine in the form of hot gasses as it comes from the combustion chamber. The kinetic energy of the gases is transferred to the rotor in the turbine by means of rotating blades.

The combustion gasses, coming from the combustion chamber or from the preceding stage, are accelerated in the stator blades to the speed while, simultaneously, the inlet pressure is reduced by vectorial addition with the circumferential speed the relative speed is obtained.

# MAIN PARTS OF GAS TURBINE

- Air intake system

- Gas turbine compressor

- Turbine

- Bypass stack and damper

- Gas turbine generator

FUEL SYSTEM OF GAS TURBINE

FUEL GAS SYSTEM

The purpose of the fuel gas system is to take gas from the custody transfer point, process it to the quality and pressure conditions required by GT and to distribute it and monitor its use.

Fuel gas system consists of the following system:

1) Off base system

2) On base system

OFF BASE FUEL GAS SYSTEM

This system is typically composed of the following:

- An Emergency Stop Valve at the Gas Inlet to the Knock – Out Drum.

- Filters

- Pressure Control Station

- Distribution piping

The emergency stop valve at the inlet to the station is provided to shut off the gas supply in an emergency. The gas fuel then goes through a knock out drum which removes the free liquid and solids from the gas stream.

The liquid separation from gas stream takes place by decreasing the gas velocity in its transit through drum. Impurities collected at the drum bottom are periodically automatically purged.

A level controller opens a valve to a drain tank from where it is vented to the atmosphere.

The filter separators have minimum of two stages of separation for removal of large liquid droplets and for mist separation. Any solid particle in gas is separated in first stage. The second stage mist separation is of vane typhoon type in which liquid separation takes place by subjecting the gas path to multiple changes of direction.

PRESSURE

Pressure is the per unit area exerted perpendicular to the surface by a liquid inside a bounding surface. Units used for pressure are Newton / m square, Pascal, bar, kg/cm square, psi, mm hg, etc

## COMBUSTION CHAMBER

Type 							: Vertical silo type

Number of combustion chambers			: 2

Number of burners per combustion			: 8

chamber

Combustion efficiency				: 99.8%

Igniter voltage						: 5000V AC

Number of bricks in combustion			: 360

Chamber

WASTE HEAT RECOVERY BOILER (WHRB)

The heat that is discharged into the atmosphere without recovering the available energy that might be economically converted into useful purpose is called waste heat and the system of heat exchangers, which converts this waste heat into a more usable form of energy, is called waste recovery system.

The basic WHRB consists of an evaporator (basic steam generator) and economizer, which heats the incoming feed water to evaporator. Super heater are also furnished and condensate preheater.

A complete WHRB would also include an inlet gas bypass damper and all interconnecting ducting between the GT exhaust stacks. Other WHRB accessories include the drum level sight glass & level controls, pressure gauges, continuous blow down control & sampling stations.

# MAIN PARTS OF WHRB

- HP super heater

- LP super heater

- HP economizer

- LP economizer

- HP evaporator

- LP evaporator

- Condensate preheater

- HP attempterator

- HP drum & LP drum

- HP circulating pump & LP circulating pump

- HP/LP boiler feed pump

## STEAM TURBINE

At Dadri, there are two modules of combined cycle gas project, each having one steam turbine generator capable of accepting the steam generated by the two WHRBs of the modules under the condition of gas turbine at their peak with design ambient temperature.

Steam turbine is a rotary machine, which converts steam jet into useful work. It consists of a nozzle, rotor & blades, steam from boiler passing through steam nozzle so its velocity increases. This high velocity steam is forced on to the rotor. The rotor contains number of blades and so rotor rotates. The turbine shaft is connected to the generator to generate the electricity. Thus turbine works as prime for generator.

The steam turbine is of BHEL make, tendon compound, one double flow HP cylinder and one double flow LP cylinder, condenser, double exhaust, reaction design having 24 reaction stages in HP cylinder and 7 recreation stages in LP cylinder, directly coupled with hydrogen cooled generator with static excitation system. Flanged rigid type couplings are used between the high pressure and low pressure rotor and both rotors are located by the auxiliary high pressure turbine thrust bearing of forced lubricated type. Turbine has two journal bearings of self spherical seated type for each of HP and LP turbine shaft. A hydraulic turning device with a speed of about 80 to 120rpm is provided to keep turbine rotating after tripping to avoid rotor bending and under other condition when unit is not running.

The allowable throttle pressure at the turbine inlet is 61.75bar with flow of 451.8/hr and temperature 528°C. When operating at peak load it generates 154-159MW with zero percent make-up and 27°C ambient temperature. However when operating at peak load turbine will generate 161.37MW with 50°C ambient temperature and 175.48MW at 5°C ambient temperature with zero percent make-up.

# MAIN PARTS OF STEAM TURBINE AND GENERATOR

- HP turbine

- LP turbine

- Generator

- Lubricating oil system

- Condenser

- Condensate extraction pump

- Cooling water pump

- Hydrogen system

- Seal oil system

GAUGES AND GAUGE PRESSURE

A gauge which uses absolute zero as datum, measures the absolute pressure.

Absolute pressure = gauge pressure + atmospheric pressure

There are different types of pressure measuring elements like

- Manometer

- Deformation pressure elements

- Differential pressure gauges

The liquid manometers (e.g. U-tube, single tube, inclined tube etc) that measures pressures directly by balancing a column of liquid against the atmospheric pressure.

DEFORMATION ELEMENTS

These devices change their shapes when pressure is applied and come back to their original shape on removal of pressure. These deformations can be converted to either mechanical movement for local indication or can be converted in to electrical or pneumatic signal for remote indication or control.

BOURDEN GAUGE

It consist of an elastic element a small volume of oval cross section bent in form of C. one end is fixed it and accept the applied pressure. When pressure is increased there is an increase in the radius of the arc. The free end which is sealed moves on application of pressure. This movement is transmitted through a sector pinion arrangement, to the pointer to be indicated on a calibrated dial. Burden tube is basically a spring that stretches when pressure is applied. The metal from which it is made has great influence on the performance of the instrument.

# DIAPHRAGM PRESSURE GAUGE

A diaphragm is a flexible disc that changes shape when the process pressure change. The diaphragm can be of rubber or stainless steel. The process pressure is given on one side of the disk the central portion of disc moves in or out according to the applied pressure, the natural spring of diaphragm pushes back against pressure.

The rigid diaphragm can be in the form of flat or corrugated plate. The deflection of a diaphragm is too small and some means of magnification is provided. One side of diaphragm serves as reference (low pressure) in which, the gauge reads pressure differential. The connection bore will be large if the process fluid is highly viscous or of slurry type. The large size bore enables easy cleaning.

This gauge is more accurate then burden gauge at low pressure. The gauge can withstand rough treatment and over heating better than burden gauge.

# CAPSULE PRESSURE GAUGE

Two diaphragms are welded together around the edge to make a capsule the inside of capsule is connected to process pressure and outside is as the reference. The outside of the capsule is exposed to the atmosphere, the instrument reads gauge pressure. The capsule can also be either a vacuum type or a process pressure type. The measuring pressure applied to the inner walls of the pointer mechanism by a shaft connected with the capsule.

# BELLOW GAUGE

Bellow is a development of a diaphragm stack. The complete element is made from single piece of seamless walled tube, sealed at one end. The bellow can be used to measure gauge differential and absolute pressures.

The process pressure is applied to the inside of the bellows and outside of the bellows is subjected to the atmospheric pressure. The top of the bellow contains precompressed calibrated spring. The applied pressure n the bellow causes it to expand. The spring gets compressed. The force of the spring opposes the force inside the bellow. The movement of the bellow is transmitted through a shaft on the top of the bellow, to the pointer. This unit measures the gauge pressure. They can also be used to indicate differential pressure and absolute pressure.

# DEAD WEIGHT TESTER

This instrument is used to calibrate pressure gauges. It uses oil to transmit pressure. It consists of an accurate machined piston, inserted in to a close fitted cylinder. The gauge to be calibrated is connected to this instrument and calibrated weights are placed at the free end of the piston by using the pump pressure is applied to the piston until enough force is developed to lift the piston weight combination. When the piston is floating freely reading on the pressure gauge is noted.

# FLOW

Flow meters & devices fall into two main groups

- Quantity or volume flow meters

- Rate meters (inferential flow meters)

# POSITIVE OR VOLUMETRIC FLOW METERS

These instrument measures flow, by transferring a measured quantity of fluid, from inlet to the outlet. They measure the quantity, which flow in a given time.

# INFERENTIAL FLOW METERS

These instrument measures the velocity of fluid from it. The volume passed is inferred. It is equal to the velocity times the cross sectional area to the flow.

Flow measuring instruments are of four types

- Mechanical flow meters

- Pressure difference flow meters

- Variable aperture flow meters

- Electro-magnetic flow meter

Pressure difference flow meters find common application for industrial use. They are capable of measuring the flow of all industrial fluids. It is possible to obtain instantaneous flow rate record of variation in flow rate & integration of the rate of the flow.

They consist of primary & secondary elements. A primary is inserted in the pipeline and generates a differential pressure the magnitude of which is proportional to the square of the rate of the flow.

There are four types to primary elements

- Ventury tube

- Orifice plate

- Flow nozzle

- Pilot tube

# VENTURY TUBES

They are used for high quantity fluid flow medium. It consists of two small hollow pipes, made in the form of cone at one end. The cones are joined by short parallel pipes.

The smallest diameter is called the throat section, where lower or down stream press is measured in the parallel pipe to the up stream. The up steam cone are made steeper, to give smooth approach to the throat section.

The down stream recovers part of the press. Differential, thus reducing over all press loss it is made of cast iron or steel.

## ORIFICE PLATE

They are used to restrict fluid flow or for differential press measurement. It consists of thin metal plate, with a hole at center & clamped between two pipes flanges. For measurement of dirty fluids or containing solid, the lower edge of the hole is confined with inside bottom of pipe. The orifice causes localized changes in velocity, which would also leads to change in pressure.

The minimum cross sectional area of the fluid is called vena contracta, which has the advantage that standard flanges can be used for the orifice plates & differential pressure is maximum for a given flow.

## FLOW NOZZLE

Flow nozzle is used to measure high velocity of stream. The extra cone is bell shaped taping are similar to ventury to tube.

The up stream is usually made about one pipe diameter from the entrance to the nozzle. The down stream tap is usually made in the pipe directly opposite the straight position of the nozzle.

ROTAMETER (variable area meter)

It is flow-measuring instrument in which pressure drop remains constant for all flow rates. The area of the opening changes as the flow rate changes. Rate of flow can be measured by the measuring the area of the opening.

Principle:

The variation in area of flow stream required to produce a constant pressure differential. At a restriction to fluid flow is proportional to the flow rate.

It consists of tapered vertical tube with a float inside. The float is made to that its largest diameter almost equal to the diameter of the tube at the bottom. The cross sectional area at the top is greater than at the bottom. Often the metering tube has protruding vertical ridges at the inside diameter for guiding the float in its travel up & down the tube.

# CONTROL VALVE ACCESSORIES

# HAND WHEEL

This can be utilized for manual operation of control valves for emergency use during startup or in the event of air failure. That are used frequently and primarily in critical services or when block & by pass valve are not located.

# LIMIT SWITCH

This is mounted on valve for their fixed travel. When the valve travels beyond the range the switch operates & stops the supply to the valve.

# AIR LOCK RELAY & SOLENOID VALVE

The output of the controller in electrical signal is 4mA to 20mA. This is given to I/P converter. This pressure signal is given to the positioner to give accurate position to the valve.

It might happen that current supply is not reached or pneumatic supply fails at that time the final control element must ensure its last position. So air lock relay is used for pneumatic failure & solenoid valve for electrical supply failure.

# SOLENOID VALVE

It consists of basically of an electromagnet and a movable armature which is a valve plug, lever, or a pilot valve. Solenoid generally provides two-position operation and when the electromagnetic is energized the armature is pulled upwards and this action opens a normally closed valve and closes a normally open valve. Solenoid operates on both A.C. & D.C.

# AIR LOCK RELAY

It has constant power supply that forces up to diaphragm port and to pass the pneumatic signal to the valve but when the pneumatic supply fails diaphragm closes the line and try to keep the last position of the FCE and the pneumatic signal is going to drain.

FINAL CONTROLELEMENTS (VALVES)

The many process control loops of the system-controlled variable are affected by manipulating the flow rate of the fluid in pipeline where sufficient pressure heads exists at the source of the flow. The rate of the flow may be maintained by increasing a variable controllable restriction that is a fluid resistance. A flow control valve performs this task and is in effect adjustable orifice.

The construction of the valve is separated in three parts-

1. VALVE ACTUATORS

This is the source of motive power to position the valve plug against the reaction of the fluid spring force.

2. VALVE BODY

This is case of the variable orifice, which is usually made of die-casting & contains the valve trim.

3. VALVE TRIM

This is the combination of the fixed valve seat & the moving plug, the relative position, which determines the area of the adjustable orifice.

## VALVE ACTUATORS

1. ELECTRO-PNEUMATIC ACTUATORS

They are a combination of an electro-pneumatic transducer and a standard air operated diaphragm or piston actuator. The transducer receives an electrical control signal generally in mA and converts those signals in to a pneumatic output pressure for operation. The output pressure is directly proportional to the input current, which is the output signal of the automatic controller.

2. PNEUMATIC ACTUATOR

A pneumatic actuator essentially is a pressure to stroke transducer. The device translates an air pressure signal into valve stem motion. The signal received by the controller actuator is transmitted by the controller directly to the actuator or indirectly through an auxiliary device such as a valve positioner or pneumatic amplifier.

Standard air signal range is between 6-30 PSIG to 3-15 PSIG. This pressure acting on the area of the actuator creates the force necessary to position the control valve.

CONTROL AND INSTRUMENTATION SYSTEM

PLANT CONTROL

The control & instrumentation system for the plant is designed to assist the operator in attainment of samples and optimum operation to the plant with maximum efficiency and to minimize the effect of failure. The design of the monitoring and control system is such as to ensure safe operation at all system loads and also permit rectification of the fault in the minimum possible time.

Self-monitoring and diagnostic feature is employed to locate the faulty component/system in minimum possible time. The control and instrumentation equipment used for the plant generally conforms to the latest available international standards.

CENTRAL CONTROL ROOM

The central control room serves as a focal point for controlling and monitoring the plant for gas turbine, waste heat recovery boilers, steam turbine and mechanical auxiliaries. The control room contains the following facilities.

- A unit control deck for each module

- An electrical control mimic board for the station power evacuation

- A backup control panel for each module, and

- A plant common services panel

PROCESS OPERATOR SYSTEM/OPERATOR INTERFACE

The plant is controlled and monitored through the operator interface. The operator interfaces are:

- Unit control desk for each module, comprising colour CRTs, keyboard for normal operation of the plant.

- One backup control panels having conventional indicators, recorders, push buttons etc. to carry out operations during CRT/keyboard failure.

- Station computer/data acquisition system with associated peripherals including colour CRT with associated keyboard, hard copier, alarm CRT, event recorders and printers to assist the operator.

A local gas turbine control and monitoring panel located in the environmentally controlled container for the open cycle operation, during the initial period till CCR is made ready. The plant control system is designed to allow control room operator to start, operate and shutdown the power generation equipment of a module. The control room operator performs all necessary functions from the operator’s console/unit control desk via colour graphic and keyboards. The operator can monitor the equipment and initiate the startup, loading and shutdown. The operator can also access the plant database for monitoring, reports, historical trends etc. from the console with the help of CRT displays and printers.

PROCESS COTROL SYSTEMS

The plant control is based on the latest and proven Teleperm ME control system, except gas turbine and steam turbine electrohydraulic control system which is based on standard and conventional Iskamatic system. Teleperm ME is microprocessor-based system. For the high availability, automation system Teleperm ME AS220EHF will be employed, which is tripple redundant central unit. The internal processing of signals is based on two out of three technologies. For limited application automation system AS220E is employed.

PROTECTIION SYSTEM

The protection system will be designed to provide practical degree of protection, while maintaining sufficient simplicity to ensure, reliability, maintainability and a minimum if nuisance trips. The trip circuits with fail safe 2 out of 3 software logic realized in the central unit AS2200 EHF. The process trip signals are applied redundantly through two channels, so that if one channel fails the protective function is maintained by automatic transfer to single channel configuration. The system will be designed to ensure complete equipment protection and maximum availability.

STEAM AND WATER ANALYSIS (SWAS)

Recognizing the importance of water chemistry in power plant operations, a comprehensive steam and water analysis system (SWAS) is envisaged for this project. The system will include a centralized water sample table for temperature and pressure reduction and conditioning of various sample stream and necessary analyzers for on line analysis of parameters like conductivity, pH, dissolved oxygen, silica, sodium etc. at all critical points in condensate feed water and steam cycle. This will help the plant chemist/operator in making the necessary adjustments in water treatment system on operating procedures so as to avoid equipment corrosion and sealing due to dissolved solids, gasses or silica.

DATA ACQUISITION SYSTEM

Data acquisition system for alarm monitoring, logging performance calculations, graphic displays etc. are provided. The central processing unit of the system is SICOMP M-26, with CRT and associated keyboard, printer each module is also provided.

NORMAL AND EMERGENCY CONTROL OF GAS TURBINE AND STEAM TURBINE

The gas turbine can be controlled during startup and loaded up to a certain preset load from the unit control center. After stabilizing at this load for couple of minute the unit control is a provision to set maximum and minimum load, rate of loading, selection of peak base mode along with all protection devices and annunciations.

The steam turbine along with its steam connections is warmed up, rolled, speeded up by an integrated automatic startup system and synchronized, the HP steam control valves are gradually opened wide.

Thus the basic control could be the fuel input for the gas turbine. The steam turbine follows the gas turbine and normally has no modulatory control and the steam pressure and temperature slide with GT load.

Thus the energy control output from the two gas turbines and a steam turbine is done by a master control at a center control console. Each GT load, however, is limited by gas turbine exhaust temperature & and intern the turbine inlet temperature. There is facility for taking over the control of units from the central to the unit control center with all annunciations to intervene during emergencies.

Normally a master control ensures that the load from the two gas turbines forming a module is formally shared. There is provision for adjustment of loading/unloading rates, setting up maximum and minimum loads and opting for operating the units on frequency control or base load mode. The excitation system of the generators in one module has arrangements at the central control room center for adjustment of reactive load on the units. These controls are naturally duplicated on unit control center.

The control center thus has the master control, two individual controls for the two gas turbines, excitation control for the three generators and auxiliary power supply system control.

PLANT MONITORING AND INFORMATION SYSTEM

The distributed digital control monitoring and information system envisaged for all this project has provision for monitoring, logging, trend display, colour coded display of real time parameters, performance evaluation, annunciation of high/low for different critical parameters, record of startup/shutdown, number of startups, development of daily load curves and the management information data. Adequate redundancies in the printers, CRT display units, trend recorders are available.

OPERATION

The station normally operates on base load. At lower loads it is envisaged to run on a module basis so that the efficiency levels are maintained. Between 80% to 100% loads, the GT units are envisaged to operate on the inlet guide vane system thereby maintaining the higher efficiency.

ELECTRICAL SYSTEM

GENERAL

Power generated from each unit is stepped up to 220KV by a step up generator transformer. Power from the 220KV switchyard is stepped up to 400KV by an auto transformer and then transmitted to northern region grid through suitable 400KV line system. Unit method connection for gas turbine generator and turbine auxiliaries is adopted.

Unit auxiliaries receive their normal power supplies at 6.6KV through one unit auxiliary transformer. For lower sized drives, 6.6KV is further stepped down to 415V by providing a number of various ratings of 6.6KV/0.415 KV auxiliary transformer. 415v switchgear further feeds number of MCCs and switchboards for running 415V drives and for the supply of LT auxiliary power.

In addition to the above, a black start diesel generator is provided for cranking and startup power requirement for the auxiliaries of one gas turbine.

All electrical equipments pertaining to gas turbine are housed in the container located in the central control gas turbine building.

AUXILIARY SYSTEM

Voltage class for auxiliaries

According to recommendation of “All India Committee on Standardization of power supply auxiliaries” primary voltage level of 6.6 KV is adopted for all large auxiliary loads above 200 KV. All other lower rated motors are connected to 415V system.

Station Power Supply Scheme

In this project, generator circuit breaker for gas turbine generator has been adopted the feature of such an arrangement is that the unit service supply for the gas turbo sets during the start up and shut down is taken from the 220 KV mains via the unit transformer and generator transformer.

When the above 220 KV supply   is not available, the black start diesel generator provides the cranking start up power for the auxiliaries of one gas turbine.

Further, lighting transformers of 415 / 415 V are also provided for the station and area lighting requirements. Automatic change over from one source to other is also envisaged in 6.6 KV level and 415 V level for all the boards.

MAIN ELECTRICAL EQUIPMENT

Turbo Generator

Dadri combined cycle gas power project consists of two modules each consisting of 2 Gas turbine generators and one steam turbine generator. Each turbo generator is of 3 phase, 2 pole, and cylindrical rotor type machine directly coupled to the steam / gas turbine rotating at 3000 rpm. Both the gas and steam turbine connected generator has the following technical parameters:

Gas Turbine				Steam Turbine

Generator					Generator

Rated Output		165.5 MVA at base load		193.1 MVA

166.3 MVA at peak load

Rated Terminal		10.5 KV				10.5 KV

Voltage

Rated Power		0.8					0.8

Factor

Rated frequency		50 Hz					50 Hz

Stator Current		9100 A				10618 A

S.C. Ratio			0.514 (min)				0.57

The machine is capable of delivering continuously output within a voltage variation of + 10% to –10% at frequency variation of +3% to -5%.

Excitation System

To have increased transient stability and capability the generator in the leading power factor zone filly static thyristorised excitation is provided.

The power requirement for generator excitation is tapped from the 6.6 KV switch gear fed from unit auxiliary transformer, stepped down, rectified in the thyristor bridges fed to the generator slip ring. During start up, the excitation system is fed from the 6.6KV station common switchgear which is fed by black start diesel-generator.

Te excitation system meets the following requirements to satisfy the system requirements as envisaged:

Range of voltage adjustment			: 0-115% (in auto and manual position)

Frequency range of operation			: 45-65 Hz

Accuracy at which generator voltage		: +-0.5 - -0.5%

is held

Response time					: 6 milliseconds

Response ratio					: 2.31 per sec.

Generator Bus Duct

The generator is connected to the generator transformer through isolated three phase bus duct. Isolated phase bus duct is of continuous enclosure type with aluminium conductor in aluminium enclosure. The main parameters of this bus duct are as follows:

Voltage rating for each run			: 10.5 KV

Current rating for GT main run			: 8594 A

Current rating for ST main run 			: 11610 Amp

Current rating for Tee off bus			: 980 Amp

Generator Transformers

The power output from each generator is stepped up to 220 KV through 166 MVA & 193 MVA Generator transformers for gas turbine and steam turbine generator respectively. These transformers are provided with manual of circuit tap changes on HV side with a range of + 10% to –2.5% in steps of 2.5%. Cooling of these transformers are ONAN / ONAF correspondingto50 / 70 / 100% rating.

Unit Auxiliary Transformer

One number, 16 MVA, 10.5 / 6.93 KV, ONAN transformer is provided for each gas turbine unit. The HV and LV terminals are connected by ducts of generator bus ducts and 6.6KV unit switchgear respectively. The transformers are provided with on Load tap changers with a range +10% to –10% in 12 steps.

6.6 KV Switchgear

The 6.6 KV switchgears are intended to supply electrical power to the 6.6 KV motors and the 6.6 KV / 415 V transformers and to ensure the protection during fault conditions. Further there is a common 6.6KV switchgear which is also fed from black start diesel generator in the event of grid failure / lack of voltage on 220 KV network.

6.6KV switchgear is indoor, metal clad, draw out type with vacuum circuit breakers. The main parameters of switchgear are

Higher system voltage 			: 7.2KV

Short time current rating	 		: 31.5KA

Short time withstand 			: 1sec

Momentary rating				: 80KA

LT TRANSFORMERS

Various LT transformers (660/415V) of different ratings are provided to meet the 415V loads of the power plant. These transformers is located indoor outdoor and shall be provided dry type mineral oi8l fill type.

LT switchgear & MCC

The LT transformer described above feeds power to the 415V switchgear which in turn distributes power to the various MCC/switchgear which are located near the load centers. The 415V switchgear is indoor non-draw on type, metal enclosed for gas turbine and WHRB and draw on type for steam turbine and station services.

D.C. systems

Each steam turbine unit has its own D.C. system located in A-D bay on 5.93m of the powerhouse. Each gas turbine unit has its own DC system located in the container. Each DC system comprises of the following:

- Storage battery

- Battery chargers

- Distribution boards

- Storage batteries

To meet the DC power requirement of various loads like DC motors, emergency lighting control and annunciation etc. of each unit during total AC power failure a storage battery of suitable capacity is provided. The emergency period i.e. the period during which no AC supply is available is taken as half hour and all batteries are designed to feed the connected loads for this period.

On this basis, the rating of 220KV battery size for steam turbine, station common & gas turbine units are 200Ah, 450Ah & 100Ah respectively.

BATTERY CHARGERS

Each battery is provided with a battery charger which is designed for float cum boost charging, that is for charging and maintaining the batteries in triple changing mode and simultaneously providing continuous DC power supply within close voltage limits.

DC DISTRIBUTION BOARD

One main DC distribution board is provided for each battery. This receives power from the battery and charger units connected to it. The DC board has required number of outgoing switchgear units to feed the loads.

BLACK START SCHEME

One diesel generating set is installed to supply startup power to one gas turbine in an event of total blackout.

Diesel generating set is of 6.6 KV, 3 phase, 50Hz, 2685 KVA with an allowable frequency variation of +5% to –5%.

PLANT INTER COMMUNICATION SYSTEM

Adequate communication facilities between operation and maintenance personnel, key personnel and P & T are made. The PA system is a two-channel voice communication system. It is composed of main station, handset station, loudspeakers and cable branching boxes.

STATION LIGHTING SYSTEM

A comprehensive lighting system is provided for the entire power station. The illumination system is designed in such a way so as to provide a uniform, reliable aesthetically pleasing glare free illumination. Illumination level to be achieved & type of fixtures being used in different areas of power plant are as indicated bellow:

The DC safety lighting system is provided at all strategic location for safe personnel movement during an emergency. This DC safety lighting system comes on automatically during failure of normal AC lighting system and standby AC lighting system. It is switched automatically after the normal AC supply has been restored & luminaries have attained then full glow.

DC safety lighting system is provided at

- Operating floors of gas turbine

- Operating floors of steam turbine

- Diesel generator

- Switchgear room

- Control and relay rooms

- Battery rooms

- Staircases

STATION GROUNDING SYSTEM

EQUIPMENT GROUNDING

Generator neutral is connected to the earth through distribution transformer provided on the neutral side.

The auxiliary system 6.6KV is operated with a resistance neutral earthing. All 220KV & 415KV system neutral is sole earthed.

SAFETY GROUNDING

Powerhouse area, switchyard area and other areas of station have efficient grounding system made of steel. The size of earthing conductor is designed to cater the maximum earth fault current for one second with exceeding specified maximum temperature at the joints. Cross section of earthing conductor includes adequate allowance for the loss of material due to corrosion over 40 years. The earthing system is designed to keep the touch potential within the safe limits.

LIGHTNING PROTECTION SYSTEM

The following direct stroke of lightning

- The main transformer and all other equipments

- 220KV switchyard

- Building, powerhouse and WHRB

The equipments listed above are protected against the direct stroke of lightning. The powerhouse building & WHRB are protected from lightning strokes by suitable lightning conductors at the top.

STARTUP POWER SUPPLY SYSTEM

The startup power supply system is obtained from the 220KV switchyard via the generator transformer, a unit auxiliary transformer and switchgear. When this supply is not available, the black start diesel generator provides the cranking and startup power for the auxiliaries on the gas turbine.

POWER AND CONTROL CABLES

All cables offered are the fire resistant, low smoke type cables. Cables of two different grades are used i.e. 6.6KV & 1.1KV.  6.6KV grade is used for 6.6KV low resistance grounded system and 1.1KV class for 415V solidly grounded system, 220V DC system and for all other control cables. 606KV grade and 1.1KV class power cables are cross linked polyethylene insulated. All power cables have stranded aluminium conductors and control cables stranded copper conductors.

THE PROTECTIVE RELAYING SYSTEM

The protective relaying systems provided for gas/steam turbine generator transformer, unit auxiliary transformer & 6.6KV auxiliaries to minimize the damage to equipments in case of faults & abnormal conditions are dealt in this section.

Generator Transformer unit

The following protections are provided for each unit:

- Generator differential protection

- Generator transformer differential protection

- Restricted Earth fault protection

- Unbalanced load protection

- Impedance protection

- Reverse power protection for gas turbines

- Stator Earth fault protection

- Rotor Earth fault protection

- Over voltage protection

- Over fluxing protection

- Frequency protection

- DC Earth fault protection

- Low forward power interlocks for steam turbine generator

- Under excitation protection

- Generator main stator Earth fault protection

Unit Auxiliary Transformer

Each unit auxiliary transformer would have the following protection:

- Transformer different protection

- Over current protection

- Single Phase inverse overcurrent time protection

6.6KV/433 Volt transformer

The LT transformer the following protection:

- Instantaneous high set overcurrent protection on all phases for short circuits.

- Instantaneous overcurrent protection for earth fault on HV side

- Overcurrent relays for protection against LV side fault

- Gas relays for alarm & trip

6.6KV Motors

The protection envisaged for 6.6KV motors is as follows:

- Instantaneous high set overcurrent relays are provided for protection against short circuit.

- Instantaneous overcurrent protection for earth fault.

- Definite time delay overcurrent relays for overload alarm.

- Locked rotor protection for motors having starting time very close to the hot stalling time.

415 V Motors

415V motors, rated bellow 110KW, is controlled by contactors and protected against short circuit and overload by HRC fuse and bimetallic overload relays respectively. Motors, rated above 110KW, are controlled by circuit breakers.

Lighting and DC circuits

All lighting and DC circuits are protected against faults by MCBs/HRC fuses. Supply failure annunciation is provided for all important circuits, while supply healthy indications are provided for less important circuits.

CONTROL CONCEPT

Electrical control board comprising of a row of free standing vertical control panels, installed in centralized control room is provided for the remote control of the electrical system including the 220KV switchyard & and general site electrical auxiliaries.

In general, the electrical control board consists of the following:

Switchyard and generator control panels for the control of:

- Each gas/system turbine generator & generator transformer.

- Each unit auxiliary transformers

- Each outgoing 220/400 KV auto transformer line.

- 220 KV bus transfer breaker

- 220 KV bus coupler breaker

Site electrical auxiliaries control panels for the control of:

- Black start diesel generator

- 6.6 KV switchboards

- 415 V centralized switchboards

- DC system

Each of these boards is provided with the necessary metering, signaling lamps & alarm windows. Independent synchronizing facility in terms of manual and automatic mode are provided for each of the gas & steam generator, each outgoing 400 KV line, 220 KV bus coupler, 220 KV bus bars etc.

NORMAL AND EMERGENCY CONTROL OF GAS TURBINE AND STEAM TURBINE

The gas turbine can be controlled during startup and loaded up to a certain preset load from the unit control center. After stabilizing at this load for couple of minute the unit control is a provision to set maximum and minimum load, rate of loading, selection of peak base mode along with all protection devices and annunciations.

The steam turbine along with its steam connections is warmed up, rolled, speeded up by an integrated automatic startup system and synchronized, the HP steam control valves are gradually opened wide.

Thus the basic control could be the fuel input for the gas turbine. The steam turbine follows the gas turbine and normally has no modulatory control and the steam pressure and temperature slide with GT load.

Thus the energy control output from the two gas turbines and a steam turbine is done by a master control at a center control console. Each GT load, however, is limited by gas turbine exhaust temperature & and intern the turbine inlet temperature. There is facility for taking over the control of units from the central to the unit control center with all annunciations to intervene during emergencies.

Normally a master control ensures that the load from the two gas turbines forming a module is formally shared. There is provision for adjustment of loading/unloading rates, setting up maximum and minimum loads and opting for operating the units on frequency control or base load mode. The excitation system of the generators in one module has arrangements at the central control room center for adjustment of reactive load on the units. These controls are naturally duplicated on unit control center.

The control center thus has the master control, two individual controls for the two gas turbines, excitation control for the three generators and auxiliary power supply system control.

PLANT MONITORING AND INFORMATION SYSTEM

The distributed digital control monitoring and information system envisaged for all this project has provision for monitoring, logging, trend display, colour coded display of real time parameters, performance evaluation, annunciation of high/low for different critical parameters, record of startup/shutdown, number of startups, development of daily load curves and the management information data. Adequate redundancies in the printers, CRT display units, trend recorders are available.

OPERATION

The station normally operates on base load. At lower loads it is envisaged to run on a module basis so that the efficiency levels are maintained. Between 80% to 100% loads, the GT units are envisaged to operate on the inlet guide vane system thereby maintaining the higher efficiency.

POWER PLANT MAINTENANCE

MAINTENANCE MANAGEMENT SYSTEM

The maintenance of this plant is carried out as per the maintenance management system of NTPC. This system aims at maximizing the availability of generating units while ensuring minimum maintenance cost, safety of plant & personnel. The maintenance management schedules detailed work specification covering all maintenance jobs permit to work system, long terms maintenance planning meeting for about 30 minutes for finalizing maintenance schedules for next 24 hours and resolution of interface problems between departments. These meetings are supplemented by meetings of HODs for one hour on alternate days to accelerate the decision making process and to lay down the properties and guidelines for maintenance work during next 72 hours.

SPARE PARTS MANAGEMENT SYSTEM

The primary objectives of the spare parts management system is to ensure timely availability of proper spare parts for efficient maintenance of the plant without excessive building up on non-moving and slow moving inventory. The spare parts management system for this plant covers the following areas:

- Proper codification of all spares and consumables

- Spare parts intending and procurement policy

- Ordering of critical mandatory and recommended spares

- Judicial fixation of inventory levels and ordering levels for spare parts based on experiments on other projects

- Development of more that one source wherever practicable

AVAILABILITY OF O&M MANUALS

- All contracts included provision of 18 sets of detailed O&M manuals which is distributed all concerned a per the approved distribution policy of the company

- The draft O&M manuals were reviewed by engineering group of task force/corporate engineering and corporate operation services to ensure completeness and proper coverage. The final manuals incorporate all NTPC comments.

- O&M manuals were available to all concerned persons at least 12 months prior to the commissioning date of the first unit to avoid problems in preparation of commissioning documents as well as proper installation & commissioning of equipments.

POLLUTION CONTROL MEASURES

GENERAL

Since it is a gas based combined cycle power project, it is least polluting as compared to coal based power station. The natural sweetened gas to be used is free sculpture and particulates. The quantity of water required and effluents generated as much less compared to coal based project of similar capacity.

WATER POLLUTION

Coal based power station require enormous quantity of water, the major requirement being cooling purpose of the steam turbine in operation. In a gas power project, only a part of the total power is generated in steam turbine, the rest being generated in the gas turbine and generators. Therefore the water requirement is much less as compared to coal based thermal power project of the same capacity.

The liquid effluents emanating from the power project are accorded appropriate treatment to control the concentration of the polluting parameters within limit.

In order to eliminate thermal discharge the power plant adopts the closed cycle cooling towers (induced draft type).

The main effluents from the power plant are pretreatment plant waste (clarifier sludge and filter backwash), demineralization plant regeneration waste, oily stream from main plant, fuel oil complex and service water. Demineralization plant regeneration waste is neutralized in a neutralization pit by dosing alkali/acid. Oil separators are provided for separation of oil. Separate oil separation pits have been constructed each for plant area, transformer yard, GT floor and fuel oil complex area, clarifier sludge and filter backwash is disposed off suitably so that suspended solid contents are contained within the discharge limit.

AIR POLLUTION

The plant has been designed to run on the natural sweetened gas. The emission is free from sulphur dioxide particulate matter. However there is contingency arrangement of HSD or fuel for four hours in a day for four days in week. Emission of NOx due to burning of natural gas can be considered as only pollutant. Burners have been designed to control the NOx emission at 50ppm. In addition to this space provision has been kept in the turbine hall for retrofitting deNOxification system by water injection, if required in future, for further reduction in emission levels. The residual gas is disposed into the atmosphere through 35m chimney.

POLLUTION MONITORING

Regular monitoring of air and water quality is undertaken after the commission of plant. The sampling location for ambient monitoring is finalized in consultation with U.P. pollution control board. Provisions have been kept in the exhaust duct of the gas turbine for stack emission.

An environmental laboratory is established at site for regular monitoring of pollution parameters. A full fledge meteorological station has been setup in the   site to record meteorological parameters. The monitoring is conducted as per the requirement of pollution control board.

CONTROL OF NOISE

The noise level of gas turbine generator sets, waste heat recovery boiler and ST generating does not exceed 85dB at 1.5m distance and 60dB at 120m distance.

CONTROL OF FIRE FAZARD

Fuel gas skid, lub. oil, HSD skid and combustion chambers are protected by CO2 flooding system in case of fire detection which is detected through automatic devices. Fire protection hydrant system and natural gas leakage automatic detector have also been provided.

GREEN BELT/AFFORESTATOPM

A thick green belt has been envisaged around the power plant complex housing gas and coal based project. The width of green belt depends on availability of space around of project complex, besides a massive afforestation has been undertaken in all available space within the plant and township area.

WATER POLLUTION MEASURES

- Cooling towers

- DM plant neutralization pit

- Oil separator

- Sewage collection treatment and disposal system (common to both coal and gas project).

AIR POLLUTION AND CONTROL MEASURES

- NOx control system

- Stack of 35m